## Slide 1: Monte Carlo Power Flow with Time-Coupled Profiles for Generating Training Datasets
P_load(t) = P_load_total × mL(t), Q_load(t) = Q_load_total × mL(t), P_PV(t) = P_PV_total × mPV(t).
Distribution to individual devices using predefined shares
D842_844ra @ 844.1: 0.25% P, 0.24% Q | M1 | Wye | 1φ
D844_846sb @ 844.2: 0.71% P, 0.57% Q | M1 | Wye | 1φ
S844 @ 844: 22.89% P, 30.17% Q | M2 | Wye | 3φ
D860_836sa @ 860.1.2 0.85% P, 0.72% Q | M1 | Delta | 1φ
…
Per-device perturbation using normal distribution & Aggregation to bus–phase nodes
844.a
p_load_kw, q_load_kvar
844.b
p_load_kw, q_load_kvar
844.a
m1_p_kw, m1_q_kvar,
…
844.b
m1_p_kw, m1_q_kvar,
…
…
…
Second solve with zero PV output to obtain vmag_zero
(Only for the fifth model)
Power flow solved using OpenDSS
vmag
At each node
vmag_delta = vmag_with_pv − vmag_zero
At each node
Training labels
Training node features
Training for all models was performed on an NVIDIA L4 GPU
Embedding vectors
Nodes and edges differ but there is only one shared message function for all edges, one shared update for all nodes.
We use node/edge features for what we can measure, and learnable embeddings for static structure not in the features.
Embeddings are updated during training via gradient descent.
Spatial and temporal error breakdown

## Slide 2: Model Comparison and Evolution
Model | Node Features | Edge Features | Additional information* | Best RMSE achieved** | Observation
1 | p_load_kw, q_load_kvar, p_pv_kw | R_full, X_full (self-impedance from impedance matrix, just for lines) | Bidirectional / with embedding vectors | 0.01653 | Worst performance in buses with capacitor bank injection and buses
2.1 | p_inj_kw, q_inj_kvar(q_load_kvar-q_cap_kvar) | Same as 1 | Bidirectional / with embedding vectors | 0.01503 | Worst performance in buses downstream of a transformer or a regulator
2.2 | Same as 2.1 | R_full, X_full (including winding resistance and leakage reactance for transformers and voltage regulators) | Bidirectional / with embedding vectors | 0.01462 | The final realized values (post-solve) are immensely different from the nominal values (pre-solve)
3.1 | m1_p_kw, m1_q_kvar, m2_p_kw, m2_q_kvar, m4_p_kw, m4_q_kvar, m5_p_kw, m5_q_kvar, q_cap_kvar, p_pv_kw | Same as 2.2 | number of training samples increased (worse performance with same number of training samples) | 0.01372 | Worst performance in buses close to the source bus
3.2 | Same as 3.1 | Same as 2.2 | Without node and edges embedding vector | 0.01589 | 
3.3 | Same as 3.1, electrical_distance_ohm, p_sys_balance_kw, q_sys_balance_kvar | Same as 2.2 | Unidirectional / with embedding vectors | 0.00912 | 
3.4 | Same as 3.2 | Same as 2.2 | Bidirectional / with embedding vectors | 0.00874 | 
4.1 | Same as 3.2, phase_onehot_1, phase_onehot_2, phase_onehot_3 | Same as 2.2 | Bidirectional / Phase as one hot feature / with embedding vectors | 0.00851 | 
4.2 | Same as 3.2 | Same as 2.2 | Bidirectional / Three different GNN trained each for one phase / with embedding vectors | 0.00801 | Training time substantially increased
5 | Same as 4.2, vmag_zero_pv_pu | Same as 2.2 | Bidirectional / Three different GNN trained each for one phase / with embedding vectors | 0.00836 | 
* all models use h_dim=32, num_layers=4, node_emb_dim=8, edge_emb_dim=4 unless otherwise specified ** in vmag_pu / vmag_delta_pu

## Slide 3: Results: OpenDSS vs GNN Predictions
24h voltage at node 852r.2: OpenDSS vs 1 vs 2.1
p_load_kw, q_load_kvar, p_pv_kw
p_inj_kw,
q_inj_kvar(q_load_kvar-q_cap_kvar)
24h voltage at node 846.3: OpenDSS vs 2.2 vs 3.1
m1_p_kw, m1_q_kvar, m2_p_kw, m2_q_kvar, m4_p_kw, m4_q_kvar, m5_p_kw, m5_q_kvar, q_cap_kvar, p_pv_kw
p_inj_kw,
q_inj_kvar
24h voltage at node 812.1: OpenDSS vs 3.1 vs 3.3
Same as 3.1, electrical_distance_ohm, p_sys_balance_kw, q_sys_balance_kvar
m1_p_kw, m1_q_kvar, m2_p_kw, m2_q_kvar, m4_p_kw, m4_q_kvar, m5_p_kw, m5_q_kvar, q_cap_kvar, p_pv_kw
24h voltage at node 848.3: OpenDSS vs 3.1 vs 3.3
Same as 3.1, electrical_distance_ohm, p_sys_balance_kw, q_sys_balance_kvar
m1_p_kw, m1_q_kvar, m2_p_kw, m2_q_kvar, m4_p_kw, m4_q_kvar, m5_p_kw, m5_q_kvar, q_cap_kvar, p_pv_kw
24h voltage at node 820.1: OpenDSS vs 3.3 vs 3.4
Bidirectional edges
Unidirectional edges
24h voltage at node 822.1: OpenDSS vs 4.1 vs 4.2
Three different GNN trained for each phase
Phase encoded as one-hot feature